## CARAT
|  | HOJA DE DATOS |  |  | MU-E50-EM/IC0024-03 de 05
|  | SERVICIO DE INGENIERIA BASICA Y DE DETALLE PUENTE DE MEDICION - SIDERURGICA MUTÚN |  |  | 1 de 2
MEDIDOR MULTIVARIABLE
ÍNDICE DE REVISIONES
FECHA | REVISION |  | OBSERVACIONES
2022-09-27 | A |  | Para Comentarios del Cliente.
2022-10-21 | B |  | Para Aprobación del Cliente.
2022-11-15 | 0 |  | Para Construcción.
Ing. Yasmani Martinez |  |  | Ing. Juan Carlos Ferrufino | Ing. William Montero
Ingeniero de Proyecto |  |  | Gerente de Ingenieria | Gerente de Proyecto
Elaborado por: |  |  | Revisado por: | Aprobado por:
ESTE DOCUMENTO ES PROPIEDAD DEGAS TRANSBOLIVIANO S.A. Y NO PODRA SER REPRODUCIDO O UTILIZADO PARA CUALQUIER FINALIDAD DIFERENTE DE AQUELLA PARA LA QUE HA SIDO SUMINISTRADO.
TIPO DE DOCUMENTO:
PROYECTO:
TITULO:
CODIGO:
HOJA:

## MVS
[5 empty] | TIPO DE DOCUMENTO: |  |  | CÓDIGO:
[5 empty] | HOJA DE DATOS |  |  | MU-E50-EM/IC0024-03 de 05
[5 empty] | PROYECTO: |  |  | HOJA:
[5 empty] | SERVICIO DE INGENIERIA BASICA Y DE DETALLE PUENTE DE MEDICION - SIDERURGICA MUTÚN |  |  | 2 de 2
[5 empty] | TÍTULO: |  |  | REV.:
[5 empty] | MEDIDOR MULTIVARIABLE |  |  | 0
GENERAL |  |  | 1 | TAG Nr. |  | (Temp. Sensor) | UE-7015 |  | (TE/TW-7015)
|  |  | 2 | Service |  |  | Puente de Medición hacia Planta Siderúrgica Mutún
|  |  | 3 | P&ID |  | Line or Vessel | MU-E50-EM-PR0003-03 de 03 |  |  | 8"-0.322-X42(G-6)-088
PROCESS CONDITIONS |  |  | 5 | Fluid |  |  | PROCESS GAS
|  |  | 6 | Fhase |  |  | GAS
|  |  | 7 | Flow (Max/Op./Min) |  |  | 63.56 / 35.31 / 24.7 MMSCFD
|  |  | 8 | Max. Pressure |  | Op. Pressure (Nor/Min) | 1420 psig |  | 870 / 640 psig
|  |  | 9 | Max. Temp. |  | Op. Temperature (Nor/Min) | 68.018 º F |  | 68 / 67.874 º F
|  |  | 10 | Op. Velocity of gas (Max/Min) |  |  | 30.29 / 11.74 ft/s
|  |  | 11 | Op. Spec. Gravity |  | Op. Viscosity | 0.619 |  | 0.013 cP
TRANSMITTER |  |  | 12 | Type |  |  | Multivariable measurement (PRESSURE & TEMPERATURE)
|  |  | 13 | Diff. Pressure Calibrated Range |  |  | N/A
|  |  | 14 | Pressure Calibrated Range |  |  | 0 - 1500 psig
|  |  | 15 | Temperature Calibrated Range |  |  | 0 - 140 º F
|  |  | 16 | Temperature Sensor |  |  | RTD - Pt 100 - According to IEC 60751 Class A
|  |  | 17 | Housing |  | Color | Low-Copper Aluminum |  | MFR Std.
|  |  | 18 | Area Classification |  |  | CLASS I, Div 1
|  |  | 19 | Enclosure Class |  |  | NEMA 4X
|  |  | 20 | Hazardous Protection |  |  | Explosion Proof
|  |  | 21 | Power Supply |  | Electrical Conn. | 24 VDC |  | 1/2 in NPT-F
|  |  | 22 | Output Signal |  |  | RS-485
|  |  | 23 | Protocol |  | Baud Rate | MVS
|  |  | 24 | Accuracy |  | Response Time | ±0.075 % de span
BODY |  |  | 26 | Process Connection |  |  | Traditional Flange w/ Manifold. 316 SST Drain/Vent valves
|  |  | 27 | Element: Type |  | Material | Diafragm |  | 316 SST
|  |  | 28 | Fill Fluid |  | Process O-Ring | Silicon |  | GLASS FILLED TFE
|  |  | 29 | Body Material |  | Drain and Vent | 316 SST |  | SST
OPTIONS |  |  | 31 | Integral Meter |  | Scale | YES - LCD Display |  | Eng. Units
|  |  | 32 | Mounting Brackets |  |  | Trad. Flange SST Bracket for 2 in. Pipe w/SST Bolts
|  |  | 33 | Lightning Protector |  |  | NO
|  |  | 34 | External Ground Screw Assy. |  |  | YES
|  |  | 35 | Hazardous Location Certification |  |  | FM Explosion Proof Approval
|  |  | 36 | Hydrostatic Testing |  |  | YES
|  |  | 37 | Calibration Test Report |  |  | YES
|  |  | 38 | SST Customer TAG Plate |  |  | YES (Legend: TAG)
MANIFOLD |  |  | 40 | Type |  | P. & Temp. Rating | 2 Valve Traditional Manifold |  | 4000 psi @ 400 °F
|  |  | 41 | Body Material |  | Process Connect. | 316 SST |  | 1/2" - NPT
|  |  | 42 | Wetted Parts |  | Packing Mat. | 316 SST |  | PTFE
|  |  | 43 | Accesories |  |  | N/A
|  |  | 45 | Manufacturer |  |  | ROSEMOUNT
|  |  | 46 | Manifold Model |  |  | 0306RT22BA11
TEMPERATURE: SENSOR & THERMOWELL |  |  | 47 | Sensor Type |  | TAG Nr. | SEE NOTA 1 |  |  |  | TE/TW-7015
|  |  | 48 | Connection Head
|  |  | 49 | Sensor Conn. |  | Electical Conn.
|  |  | 50 | Sensor Length
|  |  | 51 | Thermowell Mat. |  | Construction
|  |  | 52 | Extension L. (T) |  | Immer. Length (U)
|  |  | 53 | Process Conn.: Size / Type / Rating
|  |  | 54 | Nipple |  | Union
|  |  | 55 | Manufacturer
|  |  | 56 | Model
PURCHASE |  |  | 57 | Manufacturer |  |  | ROSEMOUNT
|  |  | 58 | Transmitter Model |  |  | 4088B1P6NG4R2A111AD4E5M5Q4
|  |  | 59 | Serial Number
|  |  | 60 | Purchase Order |  | Item
Notes:
| 1.- | El medidor multivariable deberá ser provisto con su sensor de temperatura, Ver el documento MU-E50-EMIC0024-02 de 05 Hoja de Datos Sensor de Temperatura.
2.- Las marcas y modelos de los equipos deberán ser marcas reconocidas y aprobadas por GTB.
Note on AC4: Las Cantidades de hojas se actualizan, no colocar manualmente.