## CARAT
|  | HOJA DE DATOS |  |  | MU-E50-EM/IC0024-01 de 05
|  | SERVICIO DE INGENIERIA BASICA Y DE DETALLE PUENTE DE MEDICION - SIDERURGICA MUTÚN |  |  | 1 de 3
HOJA DE DATOS DE MEDIDOR DE FLUJO
ÍNDICE DE REVISIONES
FECHA | REVISION |  | OBSERVACIONES
2022-09-27 | A |  | Para Comentarios del Cliente.
2022-10-21 | B |  | Para Aprobación del Cliente.
2022-11-15 | 0 |  | Para Construcción.
Ing. Yasmani Martinez |  |  | Ing. Juan Carlos Ferrufino | Ing. William Montero
Ingeniero de Proyecto |  |  | Gerente de Ingenieria | Gerente de Proyecto
Elaborado por: |  |  | Revisado por: | Aprobado por:
ESTE DOCUMENTO ES PROPIEDAD DE GAS TRANSBOLIVIANO S.A. Y NO PODRA SER REPRODUCIDO O UTILIZADO PARA CUALQUIER FINALIDAD DIFERENTE DE AQUELLA PARA LA QUE HA SIDO SUMINISTRADO.
TIPO DE DOCUMENTO:
PROYECTO:
TITULO:
CODIGO:
HOJA:

## FT7515
|  |  |  | TIPO DE DOCUMENTO: | MU-E50-EMIC0024-01 de 05 |  | CÓDIGO:
|  |  |  | HOJA DE DATOS |  |  | MU-E50-EM/IC0024-01 de 05
|  |  |  | PROYECTO: |  |  | HOJA:
|  |  |  | SERVICIO DE INGENIERIA BASICA Y DE DETALLE PUENTE DE MEDICION - SIDERURGICA MUTÚN |  |  | 2 de 3
|  |  |  | TÍTULO: |  |  | REV.:
|  |  |  | HOJA DE DATOS DE MEDIDOR DE FLUJO |  |  | 0
GENERAL |  | 1 | Tag Number |  |  | FIT-7015
|  | 2 | Service |  |  | Puente de Medición hacia Planta Siderúrgica Mutún
|  | 3 | Line No. / Vessel No. |  |  | 8"-0.322-X42(G-6)-088
|  | 4 | Quantity |  |  | One
|  | 5 | P&ID |  |  | MU-E50-EM/PR003-03 de 03
METERING ELEMENT |  | 6 | CONN. |  | Line Size, Sched. | 8" SCH 40 ANSI Class 600
|  | 7 |  |  | Line Material | Carbon Steel
|  | 8 |  |  | Connection Type | Flange 600 ANSI class RF
|  | 9 |  |  | Connection Mtls. | Carbon Steel
|  | 10 | METER |  | Material Body/Flange | Carbón Steel
|  | 12 |  |  | Transducer Type | Extractable, Type Chordal Design
|  | 13 |  |  | Transducer Qty | 8 transducer (4 path) as minimum
|  | 14 |  |  | Power Supply | 24 Vdc
|  | 15 |  |  | Enclosure Class | Class I, Div 1
|  | 16 |  |  | Application | Custody Transfer
|  | 17 |  |  | Accuracy | ± 0.1% of Reading
|  | 18 |  |  | Repeatability | ± 0.05% of Reading
|  | 19 |  |  | Pressure Sensor Location | On Meter Body
|  | 20 |  |  | Path Trajectory | Direct
|  | 21 |  |  | Enclosure Class | NEMA 4
|  | 22 |  |  | Prot. EEx | Explosion Proof
|  | 23 |  |  | Approval of Metrology | OIML R137-1&2 Edition 2012E - Class 0.5
|  | 24 |  |  | Meter Meets or Exceeds | AGA 9 2022 Edition / ISO 17089
|  | 25 | I/O INTERFACE |  | Communication | Ethernet Port (TCP/IP) 100Base T
|  | 26 |  |  |  | -
|  | 27 |  |  | Frequency Output | TTL/Open Collector - User Configurable
|  | 28 |  |  | Measuring Function | Flow Velocity
|  | 29 |  |  | Ouput Calculation | Volumetric Flow
|  | 30 | OPTIONS |  | Local Display | Yes
|  | 31 |  |  | Flow Conditioner | Yes (By Vendor)
|  | 32 |  |  | Config. Port | Yes
|  | 33 | PURCHASE |  | Manufacturer | -
|  | 34 |  |  | Model | -
PROCESS |  | 35 | Fluid |  |  | Natural Gas
|  | 36 | Design Flow |  |  | 63.56 MMSCFD
|  | 37 | Design Temperature |  |  | 100 °F
|  | 38 | Design Pressure |  |  | 1420 PSIG
|  | 39 | Operative Flow Max / Nor / Min |  |  | 63.56 / 35.31 / 24.7 MMSCFD
|  | 40 | Operative Pressure Max / Nor / Min |  |  | 1420 / 870 / 640 PSIG
|  | 41 | Operative Temperature Max / Nor/ Min |  |  | 68.018 / 68 / 67.874 °F
|  | 42 | Velocity Max / Min |  |  | 30 / 11.74 ft/seg
|  | 43 | Specific Gravity |  |  | 0.619
|  | 44 | Density |  |  | 2.752 lb/ft3
|  | 45 | Viscosity |  |  | 0.013 cP
Notes:
1.- La calibración del medidor ultrasónico deberá ser realizada en fabrica por el proveedor, y deberá entregar el certificado de calibración por un laboratorio acreditado.
2.- La señal de salida de pulso será conectada al computador de flujo, alimentado en 24 VDC.
3.- El proveedor deberá verificar y certificar el dimensionamiento del medidor para las condiciones de procesos indicadas en la presente hoja de datos.
3.- El proveedor deberá incluir en su provisión el software Meterlink (MeterLink Diagnostic Software) del medidor en ultima versión.
Note on AF4: Las Cantidades de hojas se actulizan, no colocar manualmente.

## METER RUN
[5 empty] | TIPO DE DOCUMENTO: |  |  | CÓDIGO:
[5 empty] | HOJA DE DATOS |  |  | MU-E50-EM/IC0024-01 de 05
[5 empty] | PROYECTO: |  |  | HOJA:
[5 empty] | SERVICIO DE INGENIERIA BASICA Y DE DETALLE PUENTE DE MEDICION - SIDERURGICA MUTÚN |  |  | 3 de 3
[5 empty] | TÍTULO: |  |  | REV.:
[5 empty] | HOJA DE DATOS DE MEDIDOR DE FLUJO |  |  | 0
METER RUN
GENERAL |  |  | 1 | Tag Number |  |  | Meter Run
|  |  | 2 | Service |  |  | Puente de Medición hacia Planta Siderúrgica Mutún
|  |  | 3 | Line No. / Vessel No. |  |  | 8"-0.322-X42(G-6)-088
|  |  | 4 | Quantity |  |  | One
|  |  | 5 | P&ID |  |  | MU-E50-EM/PR003-03 de 03
|  |  | 6 | Manufacturer |  |  | -
FLUID DATA |  |  | 7 | Fluid |  |  | Natural Gas
|  |  | 8 | Design Flow |  |  | 63.56 MMSCFD
|  |  | 9 | Operative Flow Max / Nor / Min |  |  | 63.56 / 35.31 / 24.7 MMSCFD
|  |  | 10 | Operative Pressure Max / Nor / Min |  |  | 1420 / 870 / 640 PSIG
|  |  | 11 | Operative Temperature Max / Nor/ Min |  |  | 68.018 / 67.874 °F
|  |  | 12 | Velocity Max / Min |  |  | 30 / 11.74 ft/seg
|  |  | 13 | Specific Gravity |  |  | 0.619
|  |  | 14 | Density |  |  | 2.752 lb/ft3
|  |  | 15 | Viscosity |  |  | 0.013 cP
|  |  | 16 | Molecular Weight |  |  | 17.9
|  |  | 17 | Specific Heat Ratio, K |  |  | 1.562
DESIGN DATA |  |  | 18 | Design Pressure |  |  | 1420 Psig
|  |  | 19 | Design Temperature |  |  | 68 °F
|  |  | 20 | ANSI Class |  |  | 600 #
|  |  | 21 | Piping Class |  |  | MU-E50-EM/ME0023-01 de 01
CONFIGURATION REQUIREMENTS |  |  | 22 | Pipe Run |  |  | Straight Tube Upstream And Down Meter
|  |  | 23 | OD |  |  | 8"
|  |  | 24 | SCH / Wall Thickness |  |  | 8" SCH 40 ANSI Class 600
|  |  | 25 | Material / Grade |  |  | Carbon Steel ASTM A106 / Gr. B ( in/out spool pipe)
|  |  | 26 | Meter Tube / Up & Down Stream |  |  | 10 Pipe Diameter Upstream And 5 Pipe Diameter Downstream (Flanged)
|  |  | 27 | Profiler |  |  | Yes
|  |  | 28 | Number of Orifices |  |  | 25
VALVES AND FITTINGS |  |  | 29 | Flanges |  |  | 8", ANSI Class 600 # RF ( input/output spool pipe)
|  |  | 30 | Block Valves |  |  | N/A
|  |  | 31 | Reducer |  |  | N/A
|  |  | 32 | Threaded connection instrument |  |  | 3/4" NPT ANSI 600 (TW/TE/)
|  |  | 33 |  |  |  | 1/2" NPT ANSI 600 (MVS)
|  |  | 34 |  |  |  | -
|  |  | 35 | Block Valves By Pass |  |  | N/A
TEST REQUIREMENTS |  |  | 36 | X Ray |  |  | Yes (Per ASME B31.3 Latest Edition)
|  |  | 37 | Magne Thic Particles |  |  | Yes (O-Let Welds, Per ASME B31.3 Latest Edition)
|  |  | 38 | Stress Relieve |  |  | Yes (Per ASME B31.3 Latest Edition)
|  |  | 39 | Hydrotest |  |  | Yes (Per ASME B31.3 Latest Edition)
|  |  | 40 | Flow Calibration |  |  | Yes (Meter Run & Ultrasonic Meter )
|  |  | 41 | Mech. Test & Certificates |  |  | Yes
Notes:
1.- El proveedor debera verificar las especificaciones del ramal de medicion de acuerdo a lo indicado en la hojas de datos y documentos de referencia.
|  | MU-E50-EM/PR0002-01 de 01 |  |  |  | PFD - Puente Medición Transferencia de Custodia Estación Mutún
|  | MU-E50-EM/PR0003-03 de 03 |  |  |  | P&ID -Puente de Medición Transferencia de Custodia Estación Mutún
|  | MU-E50-EM/IC0018-01 de 02 |  |  |  | Arquitectura del Control (Actualización)
|  | MU-E50-EM/ME0023-01 de 01 |  |  |  | Especificación Clase de Tuberías, Válvulas y Accesorios (Piping Class)
|  | MU-E50-EM/PR0022-02 de 02 |  |  |  | Memoria de Cálculo - Líneas de Proceso
Note on AH4: Las Cantidades de hojas se actulizan, no colocar manualmente.